| Location | January | February | March | April | May | June |
| --- | --- | --- | --- | --- | --- | --- |
| Hot | Cold | Hot | Cold | Hot | Cold | Hot | Cold | Hot | Cold | Hot | Cold |
| Kitchen Area Sink Tap | 53 | 15.7 | 55.6 | 14.6 | 57.2 | 14 | 60.4 | 14.5 | 60.1 | 18.3 |  |  |
| Kitchen Area Brita Tap | 90.1 |  Brita non functional and on repair | 89.9 | 11.6 | 90.4 | 10.1 | 91.1 | 10.2 | 90.3 | 11.6 |  |  |
| Ambient room temperature |  |  | 15.6 |  | 15.7 |  | 15.7 |  | 19 |  |  |  |
| Room Temperature  |  |  |  |  |  |  | 22.8 |  | 21 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |
| Initials/Date | AP | AP | SF | SF |  |  |

## Monitoring Tables – Monthly Temperature Monitoring Results

**Site: Unit 26 (2.06) Newark Works 2 Foundry Lane BA2 3GZ Year: 2025**

**Note:**

1. Hot temperatures should be checked for up to one minute and reach 50 oC minimum.
2. Cold temperatures should be checked for up to two minutes to fall below 20 oC.

| Location | July | August | September | October | November | December |
| --- | --- | --- | --- | --- | --- | --- |
| Hot | Cold | Hot | Cold | Hot | Cold | Hot | Cold | Hot | Cold | Hot | Cold |
| Kitchen Area Sink Tap |  |  |  |  |  |  |  |  |  |  |  |  |
|  Kitchen Aea Brita Tap |  |  |  |  |  |  |  |  |  |  |  |  |
| Tepid (room temp) |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |
| Initials/Date |  |  |  |  |  |  |

## Monitoring Tables – Monthly Temperature Monitoring Results

**Site: Year: 2025**

**Note:**

1. Hot temperatures should be checked for up to one minute and reach 50 oC minimum.
2. Cold temperatures should be checked for up to two minutes to fall below 20 oC.